## Slide 2: There are important data quality issues that suggest treating the following statements as not conclusive
It has been required to review the data acquisition system to check if it has been a data quality issue.
DC generation in power plant 1 is around 10 times higher than in plant 2
DC power generated by plant [kW]
95%
10%
Plant efficiency throughout the day [%]
PENDING A SECOND REVIEW

## Slide 3: Both power plants receive high and similar amount of irradiance, with no sign of power availability problems
The small difference found between both power plants suggest that they should have very similar DC power generation capabilities.
Total irradiance by plant [kW/m2]
PLANT 1
PLANT 2
Mean ambient temperature [ºC]
Mean modules’ temperature [ºC]
758
726
28
26
32.7
31.1

## Slide 4: DC power generation in plant 1 is very high, on the scale of 10 MW daily generation
Plant 1 and plant 2 have the same number of inverters but the DC power produced is around 10 times higher for plant 1. It is suspected that DC power generation in plant 1 is not measured correctly or artificially scaled up.
Mean hourly DC power generation by day [kW]
10,000 kW
600 kW
PLANT 1
PLANT 2

## Slide 5: There are some inverters in plant 2 that do not produce DC power 30% of the time during irradiance peak hours
It is highly suggested to check those inverters from plant 2 in the next maintenance check.
Mean inverters’ efficiency [%] distribution between 09:00 and 15:00
PLANT 2

## Slide 6: After carrying out the data analysis, the following action plan is suggested:
Data quality
PLANT 1
PLANT 2
ACTION #1: Overall data acquisition process check
Irradiance
DC Production
Inverters’ efficiency
ACTION #2:
ACTION #3: Maintenance of all inverters from plant 1 and the selected inverters from plant 2.